MICROGRID ENERGY MANAGEMENT SYSTEM

Smart Load Sharing with Priority-Based Control

Project Workflow Document — B.Tech Electrical Engineering | 3rd Year

⚠️ DOCUMENT STATUS CORRECTION — READ FIRST Previous versions of this document incorrectly stated that battery storage had been removed from scope. This was an error. Person A’s MATLAB code (Microgrid_code.m) has ALREADY IMPLEMENTED battery storage with full SOC tracking, charge/discharge logic, and a rule-based EMS across 6 simulation cases. Additionally, the document previously listed Fuzzy Logic as assigned to Person B (Python). After review, this assignment is CONFIRMED as correct and is explained in detail in Section 3A below. Person B must read Section 3A carefully before starting any work.

| Tool | Responsibility |
| --- | --- |
| MATLAB / Simulink (Person A) | Electrical circuit simulation + rule-based EMS + data export |
| Python (Person B) | Fuzzy Logic EMS, priority allocator, cost analysis, all plots |

# 1. Project Overview

This project models and simulates a Microgrid Energy Management System (EMS) that intelligently distributes power among a grid source, a solar PV array, a battery bank, and multiple loads with different priority levels. The simulation covers six distinct operating scenarios. The EMS decision logic is layered: Person A implements a rule-based controller in MATLAB to generate the simulation data, while Person B implements a Fuzzy Logic controller in Python to intelligently re-dispatch power allocation using that data.

## 1.1 Core Features

- Grid + Solar PV + Battery as three power sources

- Six simulation cases: residential, industrial, high_solar, low_solar, small_battery, large_battery

- Rule-based EMS in MATLAB (Person A) — already implemented

- Fuzzy Logic EMS controller in Python (Person B) — pending

- Priority-based load shedding when power is insufficient

- Peak shaving: cap grid draw below a defined threshold

- Energy cost model: compare Rs/kWh cost with vs without EMS

- SOC (State of Charge) tracking for battery across all simulation time

## 1.2 What Is Explicitly Out of Scope

The following are intentionally excluded from this project: 1. Grid failure / islanding scenarios and inverter resynchronisation 2. Battery degradation modelling 3. Transfer switch control and hardware implementation These are documented in Section 8 as Future Scope.

# 2. Tech Stack

## 2.1 MATLAB / Simulink (Person A)

| Component | Simulink Block | Purpose |
| --- | --- | --- |
| AC Grid | AC Voltage Source | 230 V, 50 Hz supply |
| Transmission Line | Series RLC Branch | R = 0.5 Ω, L = 1 mH line |
| Solar PV | Controlled Current Source | Irradiance-based variable input |
| Battery | Controlled Current Source + SOC logic | 48 V bank, SOC-limited dispatch |
| Variable Loads | Parallel RLC Load x2 | Step-changing demand blocks |
| Measurement | Voltage + Current Sensor | Log P, V, I, SOC |
| Export | writetable() to .csv | 6 CSV files, one per case |

## 2.2 Python (Person B)

| Library | Version | Used For |
| --- | --- | --- |
| NumPy | 1.24+ | Power balance math, array operations |
| Pandas | 2.0+ | Load simulation CSV data from Person A |
| Matplotlib | 3.7+ | All result plots and graphs |
| SciPy | 1.10+ | Signal processing, integration |
| scikit-fuzzy | 0.4+ | Fuzzy logic membership functions and rules |

# 3. Fuzzy Logic — Assignment Decision and Rationale

✅ DECISION: Fuzzy Logic stays in Python (Person B) Person A should NOT add fuzzy logic to the MATLAB code. The reasons are detailed below.

## 3.1 Why NOT in MATLAB (Person A)

- MATLAB’s Fuzzy Logic Toolbox is a paid, separately licensed add-on. Not all installations have it. scikit-fuzzy in Python is entirely free.

- Person A’s MATLAB code already implements a clean rule-based EMS using threshold logic and SOC limits. Adding fuzzy logic on top would mix two controller paradigms in a single file, making the code harder to understand and debug.

- The MATLAB code’s purpose is to model the electrical circuit and generate time-series data. Keeping EMS intelligence separate from circuit simulation is better software design.

- Person A already exports all required signals (Load, Solar, Battery, Grid, SOC) in CSV format — everything Person B needs to run the fuzzy controller is already available.

- Merging fuzzy logic into MATLAB would require redesigning the loop structure, the export pipeline, and potentially the Simulink model — wasted effort at this stage.

## 3.2 Why YES in Python (Person B)

- scikit-fuzzy is mature, well-documented, and designed exactly for this task. Membership functions, antecedents, consequents, and defuzzification are all handled with simple, readable Python code.

- Person B’s Python script reads the CSV outputs from Person A and re-runs the EMS decision at each timestep. The fuzzy logic replaces or runs alongside the rule-based EMS for direct comparison.

- Python allows Person B to compare fuzzy vs. rule-based decisions side-by-side in the same plot, which is a key insight for the report.

- All plotting, cost analysis, and report generation is already in Python. Adding fuzzy logic here keeps the entire analysis pipeline in one place.

- If parameters need tuning (e.g. changing membership function shapes), it is much faster to iterate in Python than to rebuild a Simulink FIS block.

## 3.3 What Person A Still Needs to Verify

Before handing off to Person B, Person A must confirm the following: 1. All 6 CSV files are exported correctly: residential_data.csv, industrial_data.csv, high_solar_data.csv, low_solar_data.csv, small_battery_data.csv, large_battery_data.csv 2. Each CSV has exactly 6 columns: Time, Load, Solar, Battery, Grid, SOC — with no NaN values. 3. SOC stays between 0.2 and 0.9 throughout — confirm the SOC limits in the EMS loop are working. 4. Solar output goes to zero before t = 3s and after approximately t = 13s, as defined in the code. 5. The Simulink model (.slx file) correctly reflects the same 6-case structure as the .m script.

# 4. Current Status — What Has Been Completed

## 4.1 Person A — COMPLETED Work

✅ Status: DONE — MATLAB simulation code is fully written

Person A has completed Microgrid_code.m, which performs the following:

- Simulates 15 seconds of microgrid operation at dt = 0.001 s (15,000 timesteps per case)

- Runs across 6 distinct cases: residential, industrial, high_solar, low_solar, small_battery, large_battery

- Models two load profiles: residential loads (P_load2 = 1500 W, P_load3 = 1200 W) and industrial loads (P_load2 = 3000 W, P_load3 = 2500 W), each with smooth exponential ramp-up curves

- Models solar PV using a sigmoid rise multiplied by a Gaussian decay, scaled per case (0.5x, 1.0x, or 1.5x), with a hard cutoff before t = 3 s

- Clips solar output to never exceed total load demand (P_solar = min(P_solar_base, P_load_total))

- Implements rule-based battery EMS: 60% of the load-solar deficit is assigned to the battery, efficiency-corrected, clamped to ±1500 W, with SOC upper limit of 0.9 and lower limit of 0.2

- Tracks battery SOC using Euler integration over the full simulation time

- Calculates P_grid as the residual: P_load - (P_solar + P_battery)

- Exports one CSV per case, 15,001 rows, 6 columns: Time, Load, Solar, Battery, Grid, SOC

## 4.2 What Person A Has NOT Done Yet

- The Simulink model (.slx) may not yet reflect the 6-case structure from the .m file — this needs to be verified and aligned

- No fuzzy logic in MATLAB — confirmed not required (see Section 3)

- Validation plots comparing the 6 CSV outputs have not been generated from MATLAB side

# 5. Person B — Full Task Specification

📋 This section is written for Person B to read and begin work immediately. All code files listed below are to be created in Python. Person A’s CSVs are your primary input.

## 5.1 Phase 3A — Rule-Based EMS Reimplementation

Deliverable: ems_rule.py

Purpose: Reimplement the same rule-based EMS that Person A has in MATLAB, but now in Python. This serves as your baseline to compare against fuzzy logic. Read one of Person A’s CSVs (start with residential_data.csv), apply the same threshold logic, and reproduce similar P_grid, P_battery, and SOC curves. Verify your Python curves match Person A’s CSV outputs before proceeding.

- Load the CSV using Pandas: df = pd.read_csv('residential_data.csv')

- Implement: P_req = 0.6 * (Load - Solar). If P_req > 0, divide by eta = 0.9. Else multiply by eta.

- Clamp P_req to [-1500, +1500] W and enforce SOC limits (0.2 to 0.9)

- Compute SOC[i] = SOC[i-1] - (P_battery[i] * dt) / 3600 / E_batt

- Compute P_grid = Load - (Solar + Battery) at each step

- Output: comparison plot overlaying your Python results on top of Person A’s CSV values

## 5.2 Phase 3B — Fuzzy Logic EMS Controller

Deliverable: ems_fuzzy.py

Purpose: Replace the 60% rule-based battery dispatch with a fuzzy inference system that smoothly decides how much battery power to deploy based on two inputs: the power deficit (Load - Solar) and the current SOC. This is the main intellectual contribution of the project.

Input Variables:

- power_deficit: range 0 to 6000 W. Membership: Low (0-1500), Medium (1000-3500), High (3000-6000)

- soc_level: range 0.0 to 1.0. Membership: Low (0-0.35), Medium (0.25-0.75), High (0.65-1.0)

Output Variable:

- battery_dispatch: range 0 to 1500 W. Membership: Low (0-500), Medium (300-900), High (700-1500)

Fuzzy Rules to implement:

- IF deficit is High AND soc is High THEN dispatch is High

- IF deficit is High AND soc is Medium THEN dispatch is Medium

- IF deficit is High AND soc is Low THEN dispatch is Low

- IF deficit is Medium AND soc is High THEN dispatch is Medium

- IF deficit is Medium AND soc is Medium THEN dispatch is Low

- IF deficit is Medium AND soc is Low THEN dispatch is Low

- IF deficit is Low THEN dispatch is Low (regardless of SOC)

Implementation steps:

- pip install scikit-fuzzy

- Define antecedents and consequent using skfuzzy.control.Antecedent / Consequent

- Add trimf or gaussmf membership functions for each variable

- Build ControlSystem and Simulation. At each timestep, set inputs and call compute()

- Use centroid defuzzification (default in scikit-fuzzy)

- After dispatch, compute SOC and P_grid exactly as in Phase 3A

- Key output to plot: fuzzy dispatch vs rule-based dispatch on the same axis across all 6 cases

## 5.3 Phase 3C — Priority Load Allocator

Deliverable: load_allocator.py

Purpose: At each timestep where total available power (P_solar + P_battery + P_grid_capped) is less than total demand, allocate power in priority order.

- Load P1 = 1500 W (lighting/emergency) — NEVER shed

- Load P2 = 2500 W (HVAC) — shed only if necessary

- Load P3 = 2000 W (EV charger) — shed first

- At each timestep: available = P_solar + P_battery; subtract P1 first; then P2; then P3

- If available runs out mid-list, partially serve that load and zero the rest

- Log every shedding event: which load, start time, end time, total energy not served

- Output: timeline bar chart showing when each load is fully served / partially served / shed

## 5.4 Phase 4 — Energy Cost Analysis

Deliverable: cost_model.py

- Tariff structure: Rs 8/kWh for peak hours (simulated as t = 6s to t = 10s in the 15s window), Rs 5/kWh for off-peak

- Energy cost = sum(P_grid[i] x tariff[i] x dt) / 1000 for all timesteps

- Run this for: (a) baseline with no EMS (P_grid = Load at all times), (b) rule-based EMS, (c) fuzzy EMS

- Report: three-row table showing total kWh from grid, total cost in Rs, and percentage saving vs baseline

- Run this cost analysis for all 6 cases and report which case benefits most from fuzzy EMS

## 5.5 Phase 5 — Required Output Plots

Deliverable: results_plots.py — all plots at 300 DPI PNG

- Plot 1 — P_grid: rule-based EMS vs fuzzy EMS vs no-EMS, for residential and industrial cases. Peak shaving must be clearly visible as a flat cap.

- Plot 2 — Battery dispatch: rule-based vs fuzzy, across all 6 cases. Show how fuzzy gives smoother discharge when SOC is low.

- Plot 3 — SOC over time: all 6 cases on one figure (2x3 subplots). Mark the 0.2 and 0.9 limit lines.

- Plot 4 — Solar contribution vs grid contribution over time for high_solar vs low_solar cases.

- Plot 5 — Priority load allocation timeline: stacked bar showing P1/P2/P3 served and shed for industrial case (worst case).

- Plot 6 — Cost comparison bar chart: baseline vs rule-based vs fuzzy, for all 6 cases.

# 6. Key Insights Person B Must Draw for the Report

This section defines what analysis must appear in the final report. Person B is responsible for deriving and quantifying all of these.

## 6.1 Fuzzy vs Rule-Based EMS Comparison

- The rule-based EMS always dispatches exactly 60% of the deficit from the battery, regardless of SOC. This means it drains the battery aggressively even when SOC is already low.

- The fuzzy EMS should dispatch less battery power when SOC is low, protecting the battery and relying more on the grid — but dispatch aggressively when SOC is high and deficit is large.

- Insight to report: Quantify how many times the rule-based EMS hits the SOC lower limit (0.2) across all cases vs how many times the fuzzy EMS does. The fuzzy EMS should hit it less often.

- Calculate: average battery utilisation efficiency = energy actually dispatched / (P_batt_max x simulation_time). Higher is better; compare rule-based vs fuzzy.

## 6.2 Solar Curtailment Insight

- In the code, P_solar is clipped to P_load at every timestep. This means solar is being curtailed whenever it exceeds load.

- Insight to report: Calculate total solar energy curtailed = integral of (P_solar_base - P_solar) dt for high_solar case. Report this in kWh and as a percentage of total solar potential.

- This curtailment would be reduced if the battery could absorb excess solar. Report this as a justification for why battery sizing matters (compare small_battery vs large_battery cases).

## 6.3 Battery Sizing Impact

- The code uses E_batt = 150 Wh (small), 300 Wh (default), and 800 Wh (large). Compare SOC trajectories across these three cases using the same load and solar profile.

- Insight to report: For the large battery case, how many fewer load-shedding events occur vs. the small battery case? Report the exact timestep count.

- Report: energy served to P3 load (EV charger) as a function of battery size. This shows the real-world value of larger storage.

## 6.4 Peak Shaving Effectiveness

- Without EMS, P_grid = P_load at all times, which peaks at 5500 W for residential and 5500 W for industrial.

- With EMS (rule-based), the battery caps the grid draw. With fuzzy EMS, the cap should be smoother and better sustained.

- Insight to report: Calculate peak grid demand reduction as a percentage. Target: at least 25-30% grid peak reduction with fuzzy EMS vs no-EMS.

## 6.5 Cost Saving Numbers

- Use the tariff model from Phase 4 to quantify the Rs saving per 15-second simulation cycle.

- Annualise: if this 15-second window represents a typical demand pattern, scale to 24-hour and 365-day savings.

- Report: tabulate which of the 6 cases gives the most cost saving with fuzzy EMS. Hypothesis: high_solar + large_battery gives maximum savings.

# 7. System Parameters — Fixed Reference Values

All simulation cases use these fixed parameters. Do not alter them between cases.

| Component | Parameter | Value | Unit |
| --- | --- | --- | --- |
| AC Grid | Nominal voltage | 230 | V RMS |
| AC Grid | Max supply capacity | 10 | kW |
| Solar PV | Peak output (default scale) | 2000 | W |
| Battery (default) | Energy capacity | 300 | Wh |
| Battery (small case) | Energy capacity | 150 | Wh |
| Battery (large case) | Energy capacity | 800 | Wh |
| Battery | Max charge/discharge rate | 1500 | W |
| Battery | Round-trip efficiency (η) | 0.90 | — |
| Battery | SOC initial | 0.50 | — |
| Battery | SOC upper limit | 0.90 | — |
| Battery | SOC lower limit | 0.20 | — |
| Load (residential) | Load 2 peak | 1500 | W |
| Load (residential) | Load 3 peak | 1200 | W |
| Load (industrial) | Load 2 peak | 3000 | W |
| Load (industrial) | Load 3 peak | 2500 | W |
| Simulation | Time range | 0 to 15 | seconds |
| Simulation | Timestep dt | 0.001 | seconds |

# 8. EMS Decision Logic — Step by Step

At every simulation timestep (dt = 0.001 s), the EMS runs through this decision sequence. Person A’s MATLAB code implements Steps 1–6. Person B’s fuzzy EMS replaces Step 3 with the fuzzy inference system.

| Step | Condition / Check | EMS Action |
| --- | --- | --- |
| 1 | Read inputs: P_solar, P_load_total, SOC | Sample all values for this timestep |
| 2 | Compute deficit = P_load - P_solar | If deficit <= 0, solar covers all load; battery charges if SOC < 0.9 |
| 3 | Rule-based (Person A): P_req = 0.6 x deficit / eta. Fuzzy (Person B): run FIS with deficit and SOC as inputs | Battery dispatch is determined. Clamp to [-1500 W, +1500 W] |
| 4 | SOC >= 0.9 and P_req < 0? | Block charging. Set P_req = 0. |
| 5 | SOC <= 0.2 and P_req > 0? | Block discharging. Set P_req = 0. Grid must cover full deficit. |
| 6 | P_grid = P_load - (P_solar + P_battery) | Grid supplies the remaining power. Log all values. |
| 7 | Update SOC, advance to t + dt | Repeat from Step 1. |

# 9. Future Scope

## 9.1 Model Predictive Control (MPC)

Replace the fuzzy logic controller with an MPC that optimises scheduling over a future time horizon using load forecasts and solar irradiance predictions. This significantly improves energy savings but requires quadratic programming solvers (e.g. CVXPY in Python).

## 9.2 Grid Islanding and UPS Switchover

When the grid fails, the EMS could automatically isolate and continue supplying loads from solar and battery in islanded mode. This requires IEEE 1547-compliant islanding detection and bidirectional inverter control. Suitable for M.Tech or funded research.

## 9.3 Real Hardware Integration

Implement the fuzzy EMS on a Raspberry Pi or Arduino with real sensors measuring actual grid/solar/load voltages and currents. The Python code developed in this project can be ported with minimal changes.

# 10. Final Deliverables Checklist

| # | Deliverable | Owner | Status | Done? |
| --- | --- | --- | --- | --- |
| 1 | Microgrid_code.m — MATLAB simulation, 6 cases, SOC tracking, rule-based EMS | Person A | DONE | ✅ |
| 2 | 6 CSV exports: residential, industrial, high_solar, low_solar, small_battery, large_battery (6 columns each) | Person A | DONE | ✅ |
| 3 | Microgrid_System.slx — Simulink model aligned with 6-case structure | Person A | VERIFY | ⚠️ |
| 4 | ems_rule.py — Python reimplementation of rule-based EMS with validation against Person A CSVs | Person B | PENDING | [ ] |
| 5 | ems_fuzzy.py — scikit-fuzzy controller with deficit + SOC inputs, centroid defuzzification | Person B | PENDING | [ ] |
| 6 | load_allocator.py — priority shedding with event log | Person B | PENDING | [ ] |
| 7 | cost_model.py — tariff-based cost model for all 6 cases, 3 EMS variants | Person B | PENDING | [ ] |
| 8 | results_plots.py — 6 result plots at 300 DPI PNG | Person B | PENDING | [ ] |
| 9 | Final report with all result numbers filled in, insight analysis (Sections 6.1 to 6.5) | Both | PENDING | [ ] |
| 10 | Presentation slides (8–10 slides) | Both | PENDING | [ ] |